Methodology Selection Tab

- Preferred weightings (Drop-down list: Default, User-defined) --- If "Non-EU" is selected, "Preferred weightings" is forced to "User-defined" [JSON HasDefaultWeightings true=Default False=User-defined]

- Preferred Service Catalogue (Drop-down list: Method A, Method B) [JSON Method]+ [Every service defined in the “MethodAServiceEnum” or “MethodBServiceEnum” enumeration (depending on what method you have declared in the “Method” field) must appear exactly once in the collection of “Services”.]

- Domains Present [JSON Presence]

  - Are the following technical building systems present in the building?

If not, are they mandatory for the new constructions in your country of residence?

1- This domain is present

2- This domain is absent but mandatory

0- This domain is absent and not mandarory

  - Heating (Drop-down list 0,1,2)

  - Domestic Hot Water (Drop-down list 0,1,2)

  - Cooling (Drop-down list 0,1,2)

  - Ventilation (Drop-down list 0,1,2)

  - Lighting (Drop-down list 0,1,2)

  - Dynamic Building Envelopr (Drop-down list 0,1,2)

  - Electricity (Drop-down list 0,1,2)

  - Electric Vehicle Charging (Drop-down list 0,1,2)

  - Monitoring and Control (Drop-down list 0,1,2)

- Assesment Date

  - Date (Input Field(Date))

Weighting Setting Section Tab (optional)

- Before navigating to the domain-specific dashboard, if "User-defined" or "Non-EU" is selected, the system will display an intermediate Weighting Settings section.

- This section is organized into two hierarchical levels to ensure full alignment with the SRI framework:

- Level 1: Impact Weighting   [JSON ImpactWeightings 0-1]

  - The sum of all 7 fields must be exactly 100% to proceed.

    - Optimise energy efficiency and overall in-use performance.

      - Energy efficiency (Input Field(%))

      - Maintenance and fault prediction (Input Field(%))

    - Adapt its operation to the needs of the occupant

      - Comfort (Input Field(%))

      - Convenience (Input Field(%))

      - Health, well-being and accessibility (Input Field(%))

      - Information to occupants. (Input Field(%))

    - Adapt to signals from the grid (energy flexibility)

      - Energy flexibility and storage. (Input Field(%))

  - default values set to zero, forcing the user to fill them in

- Level 2: Domain Weighting per Impact Category (Multi-tabbed)  [JSON DomainWeightings 0-1]

  - For each of the 7 Impact Categories listed above, a sub-tab is generated where the user assigns weights to the Domains:

    - Heating (Input Field(%))

    - Domestic Hot Water (Input Field(%))

    - Cooling (Input Field(%))

    - Ventilation (Input Field(%))

    - Lighting ((Input Field(%))

    - Dynamic Building Envelopr (Input Field(%))

    - Electricity (Input Field(%))

    - Electric Vehicle Charging (Input Field(%))

    - Monitoring and Control (Input Field(%))

  - The sum in each sub-tab is presented and must be 100%.

  - default values set to zero, forcing the user to fill them in

- The "Next" button remains disabled until all levels (Pillars, Impacts, and Domain-Impact sets) independently satisfy the 100% sum requirement.

Domains multi-tabbed dashboard

- Following the “General Information’s section (or the weighting setting section for some users), the interface will navigate to a multi-tabbed dashboard (e.g., Heating, DHW, etc.)

- The visibility of these tabs is determined by the "Domain Present" status selected in the General Information section: [JSON Level]

  - If 1 (Present): The domain tab is fully visible and interactive.

  - If 2 (Absent but Mandatory): The domain tab is hidden. The system flags the domain as ¨Absent but Mandatory¨ in the JSON (Presence: 2). – we will have the values only as readable for the user

  - If 0 (Absent and Not Mandatory): The domain tab is hidden and entirely excluded from the calculation.

  - Otherwise -1 based on the switch bellow

- The content within these tabs is dynamic. The system will display specific service categories and level descriptions based on the user's SRI Method selection

- Certain categories remain hidden if Method A is selected (e.g. H2d: Sequencing of different heat generators)

- For services appearing in both methods, the dropdown text for functionality levels will update to match the specific technical definitions of the selected Method.

- Each category starts with a Yes/No switch button labeled "Applicable."

  - If No: The category is excluded from the calculation.

    - Affect Maximum Obtainable Score? (Checkbox) ." [JSON Triage]

    - Functionality Level: -1 [JSON Level -1]

    - Compliance (Share %): 100% [JSON Compliance 1]

    - (“Functionality level-1 corresponds to not applicable service. If that is the case, then the compliance must be 100% for that level, and no other functionality level can appear.”)

  - If Yes: [JSON Compliance 0-1]

    - A drop-down list with the levels and a "Share %" input field (default value: 100) are revealed.

    - If the user enters a " Compliance " value of less than 100%, the system automatically generates a new row (Drop-down list + Share Input) to account for the remaining percentage.

    - This process repeats (adding Level + Compliance sets) as long as the cumulative " Compliance " total is less than 100%.

    - The system must prevent the user from moving to the next domain tab if the cumulative Compliance % of the current domain is not exactly 100%

    - [JSON Triage=True]

- Heating

  - H1a: Heat emission control (Levels 0-4)

    - Level 0: No automatic control

    - Level 1: Central automatic control (e.g. central thermostat)

    - Level 2: Individual room control (e.g. thermostatic valves or electronic controller)

    - Level 3: Individual room control with communication between controllers and to BACS

    - Level 4: Individual room control with communication and occupancy detection

  - H1b: Emission control for TABS (heating mode) (Method B Only, Levels 0-3)

    - Method B Only

    - Level 0: No automatic control

    - Level 1: Central automatic control (e.g. central thermostat)

    - Level 2: Advanced central automatic control

    - Level 3: Advanced central automatic control with intermittent operation and/or room temperature feedback control

  - H1c: Control of distribution fluid temperature (Levels 0-2)

    - Method A:

    - Level 0: None

    - Level 1: HW storage vessels available

    - Level 2: HW storage vessels controlled based on external signals (from BACS or grid)

    - Method B:

    - Level 0: No automatic control

    - Level 1: Outside temperature compensated control

    - Level 2: Demand-based control

  - H1d: Control of distribution pumps in networks (Method B Only, Levels 0-4)

    - Method B Only

    - Level 0: No automatic control

    - Level 1: On-off control

    - Level 2: Multi-stage control

    - Level 3: Variable speed pump control (internal estimation)

    - Level 4: Variable speed pump control (external demand signal)

  - H1f: Thermal Energy Storage (TES) for heating (Method B Only, Levels 0-3)

    - Method B Only

    - Level 0: Continuous storage operation

    - Level 1: Time-scheduled storage operation

    - Level 2: Load prediction-based storage operation

    - Level 3: Heat storage capable of flexible control through grid signals (e.g. DSM)

  - H2a: Heat generator control (non-heat pumps) (Levels 0-2)

    - Level 0: Constant temperature control

    - Level 1: Variable temperature control depending on outdoor temperature

    - Level 2: Variable temperature control depending on the load

  - H2b: Heat generator control (for heat pumps) (Levels 0-3)

    - Level 0: On/Off-control of heat generator

    - Level 1: Multi-stage control of heat generator capacity depending on the load or demand

    - Level 2: Variable control of heat generator capacity depending on the load or demand

    - Level 3: Variable control of heat generator capacity depending on the load and external signals from grid

  - H2d: Sequencing of different heat generators (Method B Only, Levels 0-4)

    - Method B Only

    - Level 0: Priority based on running time only

    - Level 1: Fixed priority list (e.g. rated energy efficiency

    - Level 2: Dynamic priority list (current efficiency, emissions, generator capacity)

    - Level 3: Dynamic priority list based on current and predicted load

    - Level 4: Dynamic priority list based on load, efficiency, emissions, capacity, and grid signals

  - H3: Reporting heating performance (Levels 0-4)

    - Method A:

    - Level 0: None

    - Level 1: Central or remote reporting of current performance KPIs (e.g. temperatures, submetering energy usage)

    - Level 2: Central or remote reporting of current performance KPIs and historical data

    - Level 3: Central or remote reporting of performance evaluation including forecasting and/or benchmarking

    - Level 4: Central or remote reporting of performance evaluation including forecasting and/or benchmarking, including predictive management and fault detection

    - Method B:

    - Level 0: None

    - Level 1: Reporting of current performance KPIs

    - Level 2: Reporting of KPIs and historical data

    - Level 3: Performance evaluation including forecasting or benchmarking

    - Level 4: Performance evaluation including predictive management and fault detection

  - H4: Flexibility and grid interaction (Method B Only, Levels 0-4)

    - Method B Only

    - Level 0: No automatic control

    - Level 1: Scheduled operation of heating system

    - Level 2: Self-learning optimal control

    - Level 3: Flexible control through grid signals (e.g. DSM)

    - Level 4: Optimised control based on predictions and grid signals (model predictive control)

- Domestic Hot Water (DHW)

  - DHW1a: Control of DHW storage charging (Electric) (Levels 0-2/3)

    - Method A:

    - Level 0: Automatic control on/off

    - Level 1: Automatic control on/off and scheduled charging enable

    - Level 2: Automatic control on/off, scheduled charging enable, and multi-sensor storage management

    - Method B:

    - Level 0: Automatic control on/off

    - Level 1: Automatic on/off + scheduled charging

    - Level 2: Scheduled charging + multi-sensor storage management

    - Level 3: Charging based on renewables or grid information (DR/DSM)

  - DHW1b: Control of DHW storage charging (General) (Levels 0-2/3)

    - Method A:

    - Level 0: None

    - Level 1: HW storage vessels available

    - Level 2: Automatic charging control based on local availability of renewables or information from grid (DR, DSM)

    - Method B:

    - Level 0: Automatic control on/off

    - Level 1: Automatic on/off + scheduled charging

    - Level 2: Charging control with demand-based temperature or multi-sensor management

    - Level 3: Charging control based on external signals (e.g. district heating grid)

  - DHW1d: Control of storage (Solar + Supplementary) (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: Manual selection of solar or heat generation

    - Level 1: Automatic control of solar (priority 1) + supplementary charging

    - Level 2: Solar priority + supplementary + demand-oriented supply

    - Level 3: Solar priority + supplementary + supply/return temperature control + multi-sensor management

  - DHW2b: Sequencing of DHW generators (Method B Only, Levels 0-4)

    - Method B Only:

    - Level 0: Priority based on running time

    - Level 1: Fixed priority list

    - Level 2: Dynamic priorities (efficiency, emissions, generator capacity)

    - Level 3: Dynamic priorities including predicted load

    - Level 4: Dynamic priorities including predicted load and grid signals

  - DHW3: Reporting DHW performance (Levels 0-4)

    - Method A:

    - Level 0: None

    - Level 1: Indication of actual values (e.g. temperatures, submetering energy usage)

    - Level 2: Actual values and historical data

    - Level 3: Performance evaluation including forecasting and/or benchmarking

    - Level 4: Performance evaluation including forecasting/benchmarking, including predictive management and fault detection

    - Method B:

    - Level 0: None

    - Level 1: Reporting of actual values

    - Level 2: Actual values + historical data

    - Level 3: Performance evaluation (forecasting/benchmarking)

    - Level 4: Performance evaluation including predictive management and fault detection

- Cooling

  - C1a: Cooling emission control (Levels 0-4)

    - Method A

    - Level 0: No automatic control

    - Level 1: Central automatic control (e.g. central thermostat)

    - Level 2: Individual room control (e.g. thermostatic valves or electronic controller)

    - Level 3: Individual room control with communication between controllers and to BACS

    - Level 4: Individual room control with communication and occupancy detection

    - Method B

    - Level 0: No automatic control

    - Level 1: Central automatic control

    - Level 2: Individual room control

    - Level 3: Room control + communication

    - Level 4: Room control + communication + occupancy detection

  - C1b: Emission control for TABS (cooling mode) (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: No automatic control

    - Level 1: Central automatic control

    - Level 2: Advanced central control

    - Level 3: Advanced central control with intermittent operation or feedback

  - C1c: Control of chilled water temperature (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: Constant temperature control

    - Level 1: Outdoor temperature compensated

    - Level 2: Demand-based control

  - C1d: Control of distribution pumps (Cooling) (Method B Only, Levels 0-4)

    - Method B Only:

    - Level 0: No automatic control

    - Level 1: On-off control

    - Level 2: Multi-stage control

    - Level 3: Variable speed pump control (internal estimation)

    - Level 4: Variable speed pump control (external demand signal)

  - C1f: Interlock (Heating/Cooling avoidance) (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: No interlock

    - Level 1: Partial interlock (minimising simultaneous heating/cooling)

    - Level 2: Full interlock (system ensures no simultaneous heating/cooling)

  - C1g: Control of Thermal Energy Storage (Cooling) (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: Continuous storage operation

    - Level 1: Time-scheduled storage operation

    - Level 2: Load prediction-based storage

    - Level 3: Cold storage with flexible control via grid signals (DSM)

  - C2a: Generator control for cooling (Levels 0-3)

    - Level 0: On/Off-control of cooling production

    - Level 1: Multi-stage control of cooling production capacity depending on load or demand

    - Level 2: Variable control of cooling production capacity depending on load or demand

    - Level 3: Variable control of cooling production capacity depending on load and external grid signals

  - C2b: Sequencing of cooling generators (Method B Only, Levels 0-4)

    - Method B Only:

    - Level 0: Priority based on running time

    - Level 1: Fixed sequencing based on loads

    - Level 2: Dynamic sequencing based on efficiency/characteristics

    - Level 3: Load prediction-based sequencing

    - Level 4: Sequencing using dynamic priorities + grid signals

  - C3: Reporting cooling performance (Levels 0-4)

    - Method A

    - Level 0: None

    - Level 1: Central or remote reporting of current performance KPIs

    - Level 2: Central or remote reporting of current performance KPIs and historical data

    - Level 3: Central or remote reporting of performance evaluation including forecasting and/or benchmarking

    - Level 4: Central or remote reporting of performance evaluation including forecasting and/or benchmarking, including predictive management and fault detection

    - Method B

    - Level 0: None

    - Level 1: Reporting of current KPIs

    - Level 2: Reporting + historical data

    - Level 3: Performance evaluation (forecasting/benchmarking)

    - Level 4: Performance evaluation + predictive management and fault detection

  - C4: Flexibility and grid interaction (Cooling) (Levels 0-4)

    - Method A

    - Level 0: No automatic control

    - Level 1: Scheduled operation of cooling system

    - Level 2: Self-learning optimal control of cooling system

    - Level 3: Cooling system capable of flexible control through grid signals (e.g. DSM)

    - Level 4: Optimized control of cooling system based on local predictions and grid signals (e.g. through model predictive control)

    - Method B

    - Level 0: No automatic control

    - Level 1: Scheduled cooling operation

    - Level 2: Self-learning optimal control

    - Level 3: Flexible cooling control via grid signals

    - Level 4: Optimised control based on predictions and grid signals (MPC)

- Ventilation

  - V1a: Supply air flow control (room level) (Levels 0-4)

    - Method A:

    - Level 0: No ventilation system or manual control

    - Level 1: Clock control

    - Level 2: Occupancy detection control

    - Level 3: Central demand control based on air quality sensors (CO2, VOC, humidity, …)

    - Level 4: Local demand control based on air quality sensors (CO2, VOC,...) with local flow from/to the zone regulated by dampers

    - Method B:

    - Level 0: No ventilation or manual control

    - Level 1: Clock control

    - Level 2: Occupancy detection

    - Level 3: Central demand control (CO2, VOC, humidity)

    - Level 4: Local demand control with zone dampers

  - V1c: Air flow/pressure control (AHU level) (Method B Only, Levels 0-4)

    - Method B Only:

    - Level 0: No automatic control: max airflow for all rooms

    - Level 1: On-off time control

    - Level 2: Multi-stage fan control

    - Level 3: Automatic flow/pressure control without pressure reset

    - Level 4: Automatic flow/pressure control with pressure reset (VFD)

  - V2c: Heat recovery control (overheating prevention) (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: No overheating control

    - Level 1: Sensor-based modulation or bypass

    - Level 2: Predictive or multi-sensor heat recovery control

  - V2d: Supply air temperature control (AHU) (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: No automatic control

    - Level 1: Constant setpoint

    - Level 2: Variable setpoint with outdoor temperature compensation

    - Level 3: Variable setpoint with load-based compensation

  - V3: Free cooling with mechanical ventilation (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: No automatic control

    - Level 1: Night cooling

    - Level 2: Free cooling with modulated airflow

    - Level 3: Enthalpy-based control (temperature + humidity)

  - V6: Reporting information regarding IAQ (Levels 0-3)

    - Method A

    - Level 0: None

    - Level 1: Air quality sensors (e.g.CO2) and real-time autonomous monitoring

    - Level 2: Real-time monitoring and historical information of IAQ available to occupants

    - Level 3: Real-time monitoring and historical information of IAQ available to occupants plus warnings on maintenance needs or occupant actions (e.g. window opening)

    - Method B

    - Level 0: None

    - Level 1: Real-time IAQ sensors

    - Level 2: Real-time & historical IAQ data to occupants

    - Level 3: IAQ info + maintenance/behaviour warnings

- Lighting

  - L1a: Occupancy control for indoor lighting (Levels 0-3)

    - Level 0: Manual on/off

    - Level 1: Manual on/off + sweeping extinction signal

    - Level 2: Automatic detection (auto on/dimmed or off)

    - Level 3: Automatic detection (manual on/dimmed or off)

  - L2: Control based on daylight levels (Method B Only, Levels 0-4)

    - Method B Only:

    - Level 0: Manual (central)

    - Level 1: Manual (per room/zone)

    - Level 2: Automatic switching

    - Level 3: Automatic dimming

    - Level 4: Scene-based dynamic lighting control

- Dynamic Building Envelope

  - DE1: Window solar shading control (Levels 0-4)

    - Method A

    - Level 0: No sun shading or only manual operation

    - Level 1: Motorized operation with manual control

    - Level 2: Motorized operation with automatic control based on sensor data

    - Level 3: Combined light/blind/HVAC control

    - Level 4: Predictive blind control (e.g. based on weather forecast)

    - Method B

    - Level 0: Manual or no shading

    - Level 1: Motorised manual control

    - Level 2: Automatic control via sensor data

    - Level 3: Integrated light/blind/HVAC control

    - Level 4: Predictive blind control (weather forecast)

  - DE2: Window open/closed control (HVAC-integrated) (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: Manual or fixed windows

    - Level 1: Open/closed detection to shut down HVAC

    - Level 2: Automated mechanical window opening

    - Level 3: Centralised coordination of windows (e.g. night free cooling)

  - DE4: Reporting envelope performance (Levels 0-4)

    - Method A

    - Level 0: No reporting

    - Level 1: Position of each product and fault detection

    - Level 2: Position of each product, fault detection, and predictive maintenance

    - Level 3: Position of each product, fault detection, predictive maintenance, real-time sensor data (wind, lux, temperature,...)

    - Level 4: Position of each product, fault detection, predictive maintenance, real-time and historical sensor data (wind, lux, temperature, ...)

    - Method B

    - Level 0: No reporting

    - Level 1: Position + fault detection

    - Level 2: Position + fault detection + predictive maintenance

    - Level 3: Predictive maintenance + real-time sensor data

    - Level 4: Predictive maintenance + real-time & historical sensor data

- Electricity

  - E2: Reporting local electricity generation (Levels 0-4)

    - Method A

    - Level 0: None

    - Level 1: Current generation data available

    - Level 2: Actual values and historical data

    - Level 3: Performance evaluation including forecasting and/or benchmarking

    - Level 4: Performance evaluation including forecasting and/or benchmarking, including predictive management and fault detection

    - Method B

    - Level 0: None

    - Level 1: Current generation data

    - Level 2: Actual values + historical data

    - Level 3: Performance evaluation

    - Level 4: Performance evaluation + predictive management/fault detection

  - E3: Storage of local generation (Levels 0-4)

    - Method A

    - Level 0: None

    - Level 1: On-site storage of electricity (e.g. electric battery)

    - Level 2: On-site storage of energy (e.g. battery or thermal storage) with controller based on grid signals

    - Level 3: On-site storage of energy with controller optimising the use of locally generated electricity

    - Level 4: On-site storage of energy with controller optimising the use of locally generated electricity and possibility to feed back into the grid

    - Method B

    - Level 0: None

    - Level 1: On-site electricity storage

    - Level 2: Storage with grid-signal control

    - Level 3: Storage optimising local generation use

    - Level 4: Storage optimising local gen. + feeding back to grid

  - E4: Optimizing self-consumption (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: None

    - Level 1: Scheduling consumption

    - Level 2: Automated mgmt of consumption based on renewable energy availability

    - Level 3: Consumption management based on predicted energy needs + renewables

  - E5: Control of CHP plant (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: CHP runtime based on schedule/load

    - Level 1: CHP influenced by renewable availability

    - Level 2: CHP based on renewables and grid signals dynamic optimisation

  - E8: Support of microgrid operation modes (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: None

    - Level 1: Automated mgmt of consumption based on grid signals

    - Level 2: Automated building-level consumption + supply to microgrid/grid

    - Level 3: Consumption + supply with limited island-mode capability

  - E11: Reporting energy storage info (Levels 0-4)

    - Method A

    - Level 0: None

    - Level 1: Current state of charge (SOC) data available

    - Level 2: Actual values and historical data

    - Level 3: Performance evaluation including forecasting and/or benchmarking

    - Level 4: Performance evaluation including forecasting and/or benchmarking, including predictive management and fault detection

    - Method B

    - Level 0: None

    - Level 1: State-of-charge (SOC) available

    - Level 2: Actual + historical data

    - Level 3: Performance evaluation

    - Level 4: Performance + predictive management

  - E12: Reporting electricity consumption (Levels 0-4)

    - Method A

    - Level 0: None

    - Level 1: Reporting on current electricity consumption on building level

    - Level 2: Real-time feedback or benchmarking on building level

    - Level 3: Real-time feedback or benchmarking on appliance level

    - Level 4: Real-time feedback or benchmarking on appliance level with automated personalised recommendations

    - Method B

    - Level 0: None

    - Level 1: Reporting current electricity consumption

    - Level 2: Real-time feedback/benchmarking (building)

    - Level 3: Real-time feedback/benchmarking (appliance)

    - Level 4: Recommendations based on appliance-level data

- Electric Vehicle (EV) Charging

  - EV15: EV Charging Capacity (Levels 0-4)

    - Method A

    - Level 0: Not present

    - Level 1: Ducting (or simple power plug) available

    - Level 2: 0-9% of parking spaces have recharging points

    - Level 3: 10-50% of parking spaces have recharging points

    - Level 4: >50% of parking spaces have recharging points

    - Method B

    - Level 0: Not present

    - Level 1: Ducting / simple power plug

    - Level 2: 0-9% of parking with chargers

    - Level 3: 10-50% of parking with chargers

    - Level 4: >50% of parking with chargers

  - EV16: EV Charging Grid balancing (Levels 0-2)

    - Method A

    - Level 0: Not present

    - Level 1: 1-way controlled charging (e.g. including desired departure time and grid signals for optimization)

    - Level 2: 2-way controlled charging (e.g. including desired departure time and grid signals for optimization)

    - Method B

    - Level 0: Not present

    - Level 1: One-way controlled charging

    - Level 2: Two-way controlled charging

  - EV17: EV Charging connectivity (Levels 0-2)

    - Method A

    - Level 0: No information available

    - Level 1: Reporting information on EV charging status to occupant

    - Level 2: Reporting information on EV charging status to occupant and automatic identification and authorisation of the driver to the charging station (ISO 15118 compliant)

    - Method B

    - Level 0: No information

    - Level 1: Reporting EV charging status

    - Level 2: Reporting + automatic driver identification (ISO 15118)

- Monitoring and Control

  - MC3: Runtime management of HVAC systems (Method B Only, Levels 0-3)

    - Method B Only:

    - Level 0: Manual setting

    - Level 1: Runtime scheduling of heating/cooling plants

    - Level 2: On-off control based on building loads

    - Level 3: Predictive/grid-based control of plants

  - MC4: Fault detection and diagnostics (Method B Only, Levels 0-3)

    - Method B Only

    - Level 0: No central fault indication

    - Level 1: Fault indication for at least two TBS

    - Level 2: Fault indication for all TBS

    - Level 3: Fault indication + diagnosing

  - MC9: Occupancy detection (connected services) (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: None

    - Level 1: Occupancy detection for individual services

    - Level 2: Central occupant detection integrated with multiple TBS

  - MC13: Central reporting of TBS and energy (Levels 0-3)

    - Method A

    - Level 0: None

    - Level 1: Central or remote reporting of real-time energy use per energy carrier

    - Level 2: Central or remote reporting of real-time energy use per energy carrier, combining TBS of at least two domains in one interface

    - Level 3: Central or remote reporting of real-time energy use per energy carrier, combining TBS of all main domains in one interface

    - Method B

    - Level 0: None

    - Level 1: Real-time energy reporting per carrier

    - Level 2: Real-time reporting combining at least two domains

    - Level 3: Real-time reporting combining all main domains

  - MC25: Smart Grid Integration (Levels 0-2)

    - Method A

    - Level 0: None no harmonisation between grid and TBS; building operated independently from grid load

    - Level 1: Demand side management possible for (some) individual TBS, but not coordinated over various domains

    - Level 2: Coordinated demand side management of multiple TBS 409

    - Method B

    - Level 0: No harmonisation with grid (building independent from grid load)

    - Level 1: DSM possible for some TBS but uncoordinated

    - Level 2: Coordinated DSM for multiple TBS

  - MC28: Reporting DSM performance (Method B Only, Levels 0-2)

    - Method B Only:

    - Level 0: None

    - Level 1: Reporting current DSM status including managed flows

    - Level 2: Reporting historical and predicted DSM status including managed flows

  - MC29: Override of DSM control (Method B Only, Levels 0-4)

    - Method B Only

    - Level 0: No DSM control

    - Level 1: DSM without override capability

    - Level 2: Manual override + reactivation

    - Level 3: Scheduled override + reactivation

    - Level 4: Scheduled override + optimised reactivation

  - MC30: Single integrated control platform (Levels 0-3)

    - Method A

    - Level 0: None

    - Level 1: Single platform that allows manual control of multiple TBS

    - Level 2: Single platform that allows automated control and coordination between TBS

    - Level 3: Single platform that allows automated control and coordination between TBS, with optimisation of energy flow based on occupancy, weather, and grid signals

    - Method B

    - Level 0: None

    - Level 1: Manual control of multiple TBS

    - Level 2: Automated control/coordination of TBS

    - Level 3: Coordinated TBS + optimisation based on occupancy, weather, and grid signals

Results tab

After the data collection and calculation process, the platform displays the final SRI assessment. The results are presented in three levels of detail:

- Overall SRI Score [JSON TotalScore]

  - SRI Rating (%): A single percentage representing the building's overall smart readiness.

  - Performance Class: A visual label (A to G) based on the overall percentage (similar to energy labels).

- high-level EPBD [JSON AggregatedScores]

  - A detailed table or/and bar chart presenting the scores for each EPBD

- Impact Scores [JSON ImpactScores]

  - A detailed table or/and bar chart presenting the scores for each impact

- Domain Scores [JSON DomainScores]

  - A detailed table or/and bar chart presenting the scores for each domain

- Detailed Score [JSON DetailedScores]

  - A detailed table (domain, impact) or/and heat map presenting the scores for each domain, impact set